## Hoja2
| SAJ Modbus Communication Protocol 2020 | [7 empty] | Document Number: J-RD-SW-G-1503001 Version: A Edition: 2.1
4.1 Definitions of Information Registers
offset | Decimal | Address | SIZE (Word) | Register_Name | Data Type | Rate | Unit | Property | Description about Register | Translate | Note
0 | 36608 | 8F00H | 1 | Type | UInt16 | 0 |  | R | Device Type |  | 0x0054: Single-phase hybrid storage inverter H1 series
2 | 36609 | 8F01H | 1 | SubType | UInt16 |  |  | R | Sub-type
4 | 36610 | 8F02H | 1 | CommProVersion | UInt16 | -3 |  | R | Communications Protocol Version
6 | 36611 | 8F03H | 10 | SN | String (20) |  |  | R | Serial Number |  | Invalid Value: 0x00
26 | 36621 | 8F0DH | 10 | PC | String (20) |  |  | R | Product Code |  | Invalid Value: 0x00
46 | 36631 | 8F17H | 1 | DV | UInt16 | -3 |  | R | Display Software Version |  | Invalid Value: 0xFFFF
48 | 36632 | 8F18H | 1 | MCV | UInt16 | -3 |  | R | Master Control Software Version |  | Invalid Value: 0xFFFF
50 | 36633 | 8F19H | 1 | SCV | UInt16 | -3 |  | R | Slave Control Software Version |  | Invalid Value: 0xFFFF
52 | 36634 | 8F1AH | 1 | DispHW_Version | UInt16 | -3 |  | R | Display Board Hardware Version |  | Invalid Value: 0xFFFF
54 | 36635 | 8F1BH | 1 | CtrlHW_Version | UInt16 | -3 |  | R | Control Board Hardware Version |  | Invalid Value: 0xFFFF
56 | 36636 | 8F1CH | 1 | PowerHWVersion | UInt16 | -3 |  | R | Power Board Hardware Version |  | Invalid Value: 0xFFFF
58 | 36637 | 8F1DH | 1 | BatNum | Uint16 | 0 |  | R | Battery numbers
4.2 Definitions of Realtime Data Registers（Optional）
offset | Decimal | Address | SIZE (Word) | Register_Name | Data Type | Rate | Unit | Property | Description about Register | Translate | Note
0 | 36352 | 8E00H | 1 | BMS1_type | UInt16 |  |  | R
2 | 36353 | 8E01H | 8 | BMS1_SN | String(16) |  |  | R
18 | 36361 | 8E09H | 1 | BMS1_software_Version | UInt16 | -3 |  | R
20 | 36362 | 8E0AH | 1 | BMS1_hardware_Version | UInt16 | -3 |  | R
22 | 36363 | 8E0BH | 1 | BAT1_type | UInt16 |  |  | R
24 | 36364 | 8E0CH | 8 | BAT1_SN | String(16) |  |  | R
40 | 36372 | 8E14H | 1 | BMS2_type | UInt16 |  |  | R
42 | 36373 | 8E15H | 8 | BMS2_SN | String(16) |  |  | R
58 | 36381 | 8E1DH | 1 | BMS2_software_Version | UInt16 | -3 |  | R
60 | 36382 | 8E1EH | 1 | BMS2_hardware_Version | UInt16 | -3 |  | R
62 | 36383 | 8E1FH | 1 | BAT2_type | UInt16 |  |  | R
64 | 36384 | 8E20H | 8 | BAT2_SN | String(16) |  |  | R
80 | 36392 | 8E28H | 1 | BMS3_type | UInt16 |  |  | R
82 | 36393 | 8E29H | 8 | BMS3_SN | String(16) |  |  | R
98 | 36401 | 8E31H | 1 | BMS3_software_Version | UInt16 | -3 |  | R
100 | 36402 | 8E32H | 1 | BMS3_hardware_Version | UInt16 | -3 |  | R
102 | 36403 | 8E33H | 1 | BAT3_type | UInt16 |  |  | R
104 | 36404 | 8E34H | 8 | BAT3_SN | String(16) |  |  | R
120 | 36412 | 8E3CH | 1 | BMS4_type | UInt16 |  |  | R
122 | 36413 | 8E3DH | 8 | BMS4_SN | String(16) |  |  | R
138 | 36421 | 8E45H | 1 | BMS4_software_Version | UInt16 | -3 |  | R
140 | 36422 | 8E46H | 1 | BMS4_hardware_Version | UInt16 | -3 |  | R
142 | 36423 | 8E47H | 1 | BAT4_type | UInt16 |  |  | R
144 | 36424 | 8E48H | 8 | BAT4_SN | String(16) |  |  | R
4.3 Definitions of Realtime Data Registers
offset | Decimal | Address | SIZE (Word) | Register_Name | Data Type | Rate | Unit | Property | Register Description | Translate | Note
0 | 16388 | 4004H | 1 | MPVMode | Uint16 |  |  | R | Inverter work mode
2 | 16389 | 4005H | 2 | HFaultMSG | Uint32 |  |  | R | Display board fault message
6 | 16391 | 4007H | 2 | MFaultMSG | Uint32 |  |  | R | Master Controller fault message
10 | 16393 | 4009H | 2 | MFaultMSG2 | Uint32 |  |  | R | Master Controller fault message2
14 | 16395 | 400BH | 2 | SFaultMSG | Uint32 |  |  | R | Slave Controller fault message
18 | 16397 | 400DH | 2 | SFaultMSG2 | Uint32 |  |  | R | Slave Controller fault message2
24 | 16400 | 4010H | 1 | SinkTempC | Uint16 | -1 | ℃ | R | Heat Sink Temperature
28 | 16402 | 4012H | 1 | GFCI | Int16 | 0 | mA | R | Earth-leakage Current
36 | 16406 | 4016H | 1 | ISO4 | UInt16 | 0 | kΩ | R | PV ISO
42 | 16409 | 4019H | 1 | ConnTime | Uint16 | 0 | s | R | Countdown to grid connection
0 | 16433 | 4031H | 1 | RGridVolt | Uint16 | -1 | V | R | R Phase Grid Voltage
2 | 16434 | 4032H | 1 | RGridCurr | Uint16 | -2 | A | R | R Phase Output Current |  | Error register name changed from ROutCurr to RGridCurr
4 | 16435 | 4033H | 1 | RGridFreq | Uint16 | -2 | Hz | R | R Phase Grid Frequency
6 | 16436 | 4034H | 1 | RGridDCI | Int16 | 0 | mA | R | R Phase Grid DC Component
8 | 16437 | 4035H | 1 | RGridPowerWatt | Uint16 | 0 | W | R | R Phase Output Active Power |  | Error register name changed from ROutPowerWatt to RGridPowerWatt
10 | 16438 | 4036H | 1 | RGridPowerVA | Uint16 | 0 | VA | R | R Phase Grid Apparent Power |  | Error Unit Changed From W to VA
12 | 16439 | 4037H | 1 | RGridPowerPF | Int16 | -3 |  | R | R Phase Grid Power Factor
42 | 16454 | 4046H | 1 | RInvVolt | Uint16 | -1 | V | R | R Phase Inverting Voltage
44 | 16455 | 4047H | 1 | RInvCurr | Int16 | -2 | A | R | R Phase Inverting Current
46 | 16456 | 4048H | 1 | RInvFreq | Uint16 | -2 | Hz | R | R Phase Inverting Frequency
48 | 16457 | 4049H | 1 | RInvPowerWatt | Int16 | 0 | W | R | R Phase Inverting Active Power
50 | 16458 | 404AH | 1 | RInvPowerVA | Uint16 | 0 | VA | R | R Phase Inverting Apparent Power
72 | 16469 | 4055H | 1 | ROutVolt | Uint16 | -1 | V | R | R Phase Output Voltage
74 | 16470 | 4056H | 1 | ROutCurr | Uint16 | -2 | A | R | R Phase Output Current
76 | 16471 | 4057H | 1 | ROutFreq | Uint16 | -2 | Hz | R | R Phase Output Frequency
78 | 16472 | 4058H | 1 | ROutDVI | Int16 | 0 | mV | R | R Phase Output Voltage DC Component
80 | 16473 | 4059H | 1 | ROutPowerWatt | Uint16 | 0 | W | R | R Phase Output Active Power
82 | 16474 | 405AH | 1 | ROutPowerVA | Uint16 | 0 | VA | R | R Phase Output Apparent Power
0 | 16487 | 4067H | 1 | BusVoltMaster | UInt16 | -1 | V | R | R Master BUS Voltage
2 | 16488 | 4068H | 1 | BusVoltSlave | UInt16 | -1 | V | R | R Slave BUS Voltage
4 | 16489 | 4069H | 1 | BatVolt | Uint16 | -1 | V | R | Battery Voltage
6 | 16490 | 406AH | 1 | BatCurr | Int16 | -2 | A | R | Battery Current
8 | 16491 | 406BH | 1 | BatCurr1 | Int16 | -2 | A | R | Battery control1 Current
10 | 16492 | 406CH | 1 | BatCurr2 | Int16 | -2 | A | R | Battery control2 Current
12 | 16493 | 406DH | 1 | BatPower | Int16 | 0 | W | R | Battery Power
14 | 16494 | 406EH | 1 | BatTempC | Int16 | -1 | ℃ | R | Battery Temperature
16 | 16495 | 406FH | 1 | BatEnergyPercent | Uint16 | -2 | % | R | Battery energy percent
20 | 16497 | 4071H | 1 | PV1Volt | UInt16 | -1 | V | R | PV1 Voltage
22 | 16498 | 4072H | 1 | PV1Curr | UInt16 | -2 | A | R | PV1 Total current
24 | 16499 | 4073H | 1 | PV1Power | UInt16 | 0 | W | R | PV1 Power
26 | 16500 | 4074H | 1 | PV2Volt | UInt16 | -1 | V | R | PV2 Voltage
28 | 16501 | 4075H | 1 | PV2Curr | UInt16 | -2 | A | R | PV2 Total current
30 | 16502 | 4076H | 1 | PV2Power | UInt16 | 0 | W | R | PV2 Power
0 | 16533 | 4095H | 1 | PV_direction | Uint16 | 0 |  | R | PV Energy Flow Direction
2 | 16534 | 4096H | 1 | Battery_direction | int16 | 0 |  | R | Battery Energy Flow Direction
4 | 16535 | 4097H | 1 | Grid_direction | int16 | 0 |  | R | Grid Power Flow Direction
6 | 16536 | 4098H | 1 | OutPut_direction | Uint16 | 0 |  | R | Energy Flow Direction ( Output to Load)
22 | 16544 | 40A0H | 1 | SysTotalLoadWatt | Int16 | 0 | W | R | Total Inverting Active Power
32 | 16549 | 40A5H | 1 | TotalPVPower | Int16 | 0 | W | R | Total Inverting Apparent Power
34 | 16550 | 40A6H | 1 | TotalBatteryPower | Int16 | 0 | W | R | Total Battery Power
36 | 16551 | 40A7H | 1 | TotalGridPowerWatt | Int16 | 0 | W | R | Total Grid Power Watt
38 | 16552 | 40A8H | 1 | TotalGridPowerVA | Int16 | 0 | VA | R | Total Grid Power VA
40 | 16553 | 40A9H | 1 | TotalInvPowerWatt | Int16 | 0 | W | R | Total Inverter Power Watt
42 | 16554 | 40AAH | 1 | TotalInvPowerVA | Int16 | 0 | VA | R | Total Inverter Power VA
44 | 16555 | 40ABH | 1 | BackupTotalLoadPowerWatt | Uint16 | 0 | W | R | Backup Total Load Power Watt
46 | 16556 | 40ACH | 1 | BackupTotalLoadPowerVA | Uint16 | 0 | VA | R | Backup Total Load Power VA
0 | 16575 | 40BFH | 2 | Today_PVEnergy | Uint32 | -2 | kWh | R | Today's PV Generation
4 | 16577 | 40C1H | 2 | Month_PVEnergy | Uint32 | -2 | kWh | R | PV Generation of the current month
8 | 16579 | 40C3H | 2 | Year_PVEnergy | Uint32 | -2 | kWh | R | PV Generation of the current year
12 | 16581 | 40C5H | 2 | Total_PVEnergy | Uint32 | -2 | kWh | R | Total PV Generation
16 | 16583 | 40C7H | 2 | Today_BatChgEnergy | Uint32 | -2 | kWh | R | Today's Energy Used for Battery Charging
20 | 16585 | 40C9H | 2 | Month_BatChgEnergy | Uint32 | -2 | kWh | R | Energy Used for Battery Charging in the current month
24 | 16587 | 40CBH | 2 | Year_BatChgEnergy | Uint32 | -2 | kWh | R | Energy Used for Battery Charging in the current year
28 | 16589 | 40CDH | 2 | Total_BatChgEnergy | Uint32 | -2 | kWh | R | Total Energy Used for Battery Charging
32 | 16591 | 40CFH | 2 | Today_BatDisEnergy | Uint32 | -2 | kWh | R | Today's Energy Discharged by Battery
36 | 16593 | 40D1H | 2 | Month_BatDisEnergy | Uint32 | -2 | kWh | R | Energy Discharged by Battery in the current month
40 | 16595 | 40D3H | 2 | Year_BatDisEnergy | Uint32 | -2 | kWh | R | Energy Discharged by Battery in the current year
44 | 16597 | 40D5H | 2 | Total_BatDisEnergy | Uint32 | -2 | kWh | R | Total Energy Discharged by Battery
64 | 16607 | 40DFH | 2 | Today_TotalLoadEnergy | Uint32 | -2 | kWh | R | Load Power Consumption of today
68 | 16609 | 40E1H | 2 | Month_TotalLoadEnergy | Uint32 | -2 | kWh | R | Load Power Consumption of the month
72 | 16611 | 40E3H | 2 | Year_TotalLoadEnergy | Uint32 | -2 | kWh | R | Load Power Consumption of the year
76 | 16613 | 40E5H | 2 | Total_TotalLoadEnergy | Uint32 | -2 | kWh | R | Total Load Power Consumption
80 | 16615 | 40E7H | 2 | Today_BackupLoadEnergy | Uint32 | -2 | kWh | R | Today’s Backup Load Energy
84 | 16617 | 40E9H | 2 | Month_BackupLoadEnergy | Uint32 | -2 | kWh | R | Backup Load Energy in the current month
88 | 16619 | 40EBH | 2 | Year_BackupLoadEnergy | Uint32 | -2 | kWh | R | Backup Load Energy in the current year
92 | 16621 | 40EDH | 2 | Total_BackupLoadEnergy | Uint32 | -2 | kWh | R | Total Backup Load Energy
96 | 16623 | 40EFH | 2 | Today_SellEnergy | Uint32 | -2 | kWh | R | Power Export to the Grid today
100 | 16625 | 40F1H | 2 | Month_SellEnergy | Uint32 | -2 | kWh | R | Power Export to the Grid in the current month
104 | 16627 | 40F3H | 2 | Year_SellEnergy | Uint32 | -2 | kWh | R | Power Export to the Grid in the current year
108 | 16629 | 40F5H | 2 | Total_SellEnergy | Uint32 | -2 | kWh | R | Total Power Export to the Grid
112 | 16631 | 40F7H | 2 | Today_FeedInEnergy | Uint32 | -2 | kWh | R | Power Imported from the Grid of today
116 | 16633 | 40F9H | 2 | Month_FeedInEnergy | Uint32 | -2 | kWh | R | Power Imported from the Grid in the current month
120 | 16635 | 40FBH | 2 | Year_FeedInEnergy | Uint32 | -2 | kWh | R | Power Imported from the Grid in the current year
124 | 16637 | 40FDH | 2 | Total_FeedInEnergy | Uint32 | -2 | kWh | R | Total Power Imported from the Grid
4.4 Definition of Primary Controller Data Registers (optional)
offset | Decimal | Address | SIZE (Word) | Register_Name | Data Type | Rate | Unit | Property | Register Description | Translate | Note
0 | 40960 | A000H | 1 | BatNum | Uint16 | 0 |  | R | Battery Number |  | BatNumber
2 | 40961 | A001H | 1 | BatCapcity | UInt16 | 0 | AH | R | Battery Capacity |  | BatCap
4 | 40962 | A002H | 1 | Bat1FaultMSG | Uint16 | 0 |  | R | Battery1 Fault Message
6 | 40963 | A003H | 1 | Bat1warningMSG | Uint16 | 0 |  | R | Battery1 warning Message
8 | 40964 | A004H | 1 | Bat2FaultMSG | Uint16 | 0 |  | R | Battery2 Fault Message
10 | 40965 | A005H | 1 | Bat2warningMSG | Uint16 | 0 |  | R | Battery2 warning Message
12 | 40966 | A006H | 1 | Bat3FaultMSG | Uint16 | 0 |  | R | Battery3 Fault Message
14 | 40967 | A007H | 1 | Bat3warningMSG | Uint16 | 0 |  | R | Battery3 warning Message
16 | 40968 | A008H | 1 | Bat4FaultMSG | Uint16 | 0 |  | R | Battery4 Fault Message
18 | 40969 | A009H | 1 | Bat4warningMSG | Uint16 | 0 |  | R | Battery4 warning Message
20 | 40970 | A00AH | 2 | Reserve | Uint16 | 0 |  | R | Reserve
24 | 40972 | A00CH | 1 | Bat1SOC | Uint16 | -2 | % | R | Battery1 SOC
26 | 40973 | A00DH | 1 | Bat1SOH | Uint16 | -2 | % | R | Battery1 SOH
28 | 40974 | A00EH | 1 | Bat1Voltage | Uint16 | -1 | V | R | Battery1 Voltage
30 | 40975 | A00FH | 1 | Bat1Current | int16 | -2 | A | R | Battery1 Current
32 | 40976 | A010H | 1 | Bat1Temperature | int16 | -1 | ℃ | R | Battery1 Temperature
34 | 40977 | A011H | 1 | Bat1CycleNum | Uint16 | 0 |  | R | Battery1 Cycle Number
36 | 40978 | A012H | 1 | Bat2SOC | Uint16 | -2 | % | R | Battery2 SOC
38 | 40979 | A013H | 1 | Bat2SOH | Uint16 | -2 | % | R | Battery2 SOH
40 | 40980 | A014H | 1 | Bat2Voltage | Uint16 | -1 | V | R | Battery2 Voltage
42 | 40981 | A015H | 1 | Bat2Current | int16 | -2 | A | R | Battery2 Current
44 | 40982 | A016H | 1 | Bat2Temperature | int16 | -1 | ℃ | R | Battery2 Temperature
46 | 40983 | A017H | 1 | Bat2CycleNum | Uint16 | 0 |  | R | Battery2 Cycle Number
48 | 40984 | A018H | 1 | Bat3SOC | Uint16 | -2 | % | R | Battery3 SOC
50 | 40985 | A019H | 1 | Bat3SOH | Uint16 | -2 | % | R | Battery3 SOH
52 | 40986 | A01AH | 1 | Bat3Voltage | Uint16 | -1 | V | R | Battery3 Voltage
54 | 40987 | A01BH | 1 | Bat3Current | int16 | -2 | A | R | Battery3 Current
56 | 40988 | A01CH | 1 | Bat3Temperature | int16 | -1 | ℃ | R | Battery3 Temperature
58 | 40989 | A01DH | 1 | Bat3CycleNum | Uint16 | 0 |  | R | Battery3 Cycle Number
60 | 40990 | A01EH | 1 | Bat4SOC | Uint16 | -2 | % | R | Battery4 SOC
62 | 40991 | A01FH | 1 | Bat4SOH | Uint16 | -2 | % | R | Battery4 SOH
64 | 40992 | A020H | 1 | Bat4Voltage | Uint16 | -1 | V | R | Battery4 Voltage
66 | 40993 | A021H | 1 | Bat4Current | int16 | -2 | A | R | Battery4 Current
68 | 40994 | A022H | 1 | Bat4Temperature | int16 | -1 | ℃ | R | Battery4 Temperature
70 | 40995 | A023H | 1 | Bat4CycleNum | Uint16 | 0 |  | R | Battery4 Cycle Number
4.5 Definition of Special Registers
| Decimal | Address | SIZE (Word) | Register_Name | Data Type | Rate | Unit | Property | Description about Register | Translate | Note | Defaults | Minimum Setting range | Maximum setting range
0 | 12808 | 3208H | 1 | SafetyType | UInt16 |  |  | R/W | Safety Type |  |  | 0x2530
2 | 12809 | 3209H | 1 | FunMask | UInt16 |  |  | R/W | Function Mask |  |  | 0xFFFF
36 | 12826 | 321AH | 1 | ReConnTime | UInt16 | 0 | S | R/W | ReConnect Time |  |  | 60 | 5 | 600
42 | 12829 | 321DH | 1 | ReactiveMode | UInt16 |  |  | R/W | Reactive Mode |  | 0 is capacitive regulation (kw), 1 is inductive regulation (kw), 2 is capacitive power factor regulation. 3 is inductive power factor regulation. 4 is curve mode | 5 | 0 | 65535
44 | 12830 | 321EH | 1 | ReactiveValue | UInt16 | -3 |  | R/W | Reactive Value |  | KW OR & | 1000 | 0 | 65535
56 | 12836 | 3224H | 1 | GridVolt10mHigh | UInt16 | -1 | V | R/W | GridVolt10mHigh |  |  | 3000 | 2400 | 3000
58 | 12837 | 3225H | 1 | GridVoltHigh | UInt16 | -1 | V | R/W | Grid Volt High |  |  | 2800 | 2400 | 3000
60 | 12838 | 3226H | 1 | GridVoltLow | UInt16 | -1 | V | R/W | Grid Volt Low |  |  | 1600 | 1000 | 2200
62 | 12839 | 3227H | 1 | GridFreqHigh | UInt16 | -2 | Hz | R/W | Grid Frequency High |  |  | 5498 | 5000 | 6500
64 | 12840 | 3228H | 1 | GridFreqLow | UInt16 | -2 | Hz | R/W | Grid FrequencyLow |  |  | 4502 | 4500 | 6000
66 | 12841 | 3229H | 1 | GridVoltHigh2 | UInt16 | -1 | V | R/W | Grid Volt High2 |  |  | 2900 | 2400 | 3000
68 | 12842 | 322AH | 1 | GridVoltLow2 | UInt16 | -1 | V | R/W | Grid Volt Low2 |  |  | 1100 | 1000 | 2200
70 | 12843 | 322BH | 1 | GridFreqHigh2 | UInt16 | -2 | Hz | R/W | Grid Frequency High2 |  |  | 5500 | 5000 | 6500
72 | 12844 | 322CH | 1 | GridFreqLow2 | UInt16 | -2 | Hz | R/W | Grid Frequency Low2 |  |  | 4500 | 4500 | 6000
74 | 12845 | 322DH | 1 | GridVoltHighTripTime | UInt16 | 0 |  | R/W | Grid Voltage High Trip Time |  |  | 90 | 0 | 65535
76 | 12846 | 322EH | 1 | GridVoltLowTripTime | UInt16 | 0 |  | R/W | Grid Voltage Low Trip Time |  |  | 90 | 0 | 65535
78 | 12847 | 322FH | 1 | GridVoltHighTripTime2 | UInt16 | 0 |  | R/W | Grid Voltage High Trip Time2 |  |  | 5 | 0 | 65535
80 | 12848 | 3230H | 1 | GridVoltLowTripTime2 | UInt16 | 0 |  | R/W | Grid Volt Low Trip Time2 |  |  | 5 | 0 | 65535
82 | 12849 | 3231H | 1 | GridFreqHighTripTime | UInt16 | 0 |  | R/W | Grid Frequency High Trip Time |  |  | 90 | 0 | 65535
84 | 12850 | 3232H | 1 | GridFreqLowTripTime | UInt16 | 0 |  | R/W | Grid Frequency Low Trip Time |  |  | 90 | 0 | 65535
86 | 12851 | 3233H | 1 | GridFreqHighTripTime2 | UInt16 | 0 |  | R/W | Grid Frequency High Trip Time2 |  |  | 90 | 0 | 65535
88 | 12852 | 3234H | 1 | GridFreqLowTripTime2 | UInt16 | 0 |  | R/W | Grid Frequency Low Trip Time2 |  |  | 90 | 0 | 65535
0 | 12871 | 3247H | 1 | AppMode | UInt16 |  |  | R/W | Application Mode |  | 0x00 Self-use 0x01 Time-Of-Use 0x03 Passive 0x02 Backup | 0 | 0 | 65535
2 | 12872 | 3248H | 1 | GridChargPowerLimit | UInt16 | 0 | W | R/W | Grid Charging Power Limit |  | Default 2500W | 2500 | 100 | 5250
4 | 12873 | 3249H | 1 | GridFeedPowerLimit | UInt16 | 0 | W | R/W | Grid Feed Power Limit |  | Default 5000W | 5000 | 100 | 5250
6 | 12874 | 324AH | 1 | BatType | UInt16 | 0 |  | R/W | Battery Type |  | Default:0，0= Lead-acid battery,1= lithium battery | 0 | 0 | 1
8 | 12875 | 324BH | 1 | BatCapacity | UInt16 | 0 | AH | R/W | Battery Capacity | Cambio de BatCapcity a BatCapacity | Default 100AH | 100 | 50 | 1000
10 | 12876 | 324CH | 1 | BatProtHigh | UInt16 | -1 | V | R/W | Battery Protection High |  | Default 60V，50~60V | 600 | 500 | 600
12 | 12877 | 324DH | 1 | BatProtLow | UInt16 | -1 | V | R/W | Battery Protection Low |  | Default 46V，40~52V | 460 | 400 | 520
14 | 12878 | 324EH | 1 | BatOpenVolt | UInt16 | -1 | V | R/W | Battery Open Volt |  | Default 38V，12~42V | 360 | 120 | 420
16 | 12879 | 324FH | 1 | BatLowVolt | UInt16 | -1 | V | R/W | Battery Low Volt |  | Default 42V，40~48V | 420 | 400 | 480
18 | 12880 | 3250H | 1 | BatDisDepth | UInt16 | 0 | % | R/W | Battery Discharging Depth |  | Default80%，20~95% | 80 | 20 | 95
20 | 12881 | 3251H | 1 | BatFloatVolt | UInt16 | -1 | V | R/W | Battery Float Volt |  | Default 54V，48~58V | 540 | 480 | 580
22 | 12882 | 3252H | 1 | BatFloatTime | UInt16 | 0 | min | R/W | Battery Float Time |  | Default 120，0~65535 | 120 | 0 | 65535
24 | 12883 | 3253H | 1 | BatChgCurrLimit | UInt16 | -1 | A | R/W | Battery Charging Current Limit |  | Default 50A，5~50A | 500 | 50 | 500
26 | 12884 | 3254H | 1 | BatDisCurrLimit | UInt16 | -1 | A | R/W | Battery Discharging Current Limit |  | Default 100A,5~120A | 1000 | 50 | 1200
28 | 12885 | 3255H | 1 | BatAutoWakeEn | UInt16 | 0 |  | R/W | Battery Auto Wake Enable |  | Default:0，0= OFF，1=ON，Allow setting only when the battery type is lithium battery | 0 | 0 | 1
30 | 12886 | 3256H | 1 | BatVoltAdjCoef | UInt16 | 0 |  | R/W | Battery Volt Auto self check |  | Default 4096（IQ12） | 4096 | 3277 | 4915
0 | 12913 | 3271H | 1 | BackModSOCRetain | UInt16 | 0 | % | R/W | Backup Mode SOC Retain |  | Default 80 | 80 | 1 | 100
2 | 12914 | 3272H | 1 | EpsModeEn | UInt16 | 0 |  | R/W | EpsModeEn |  | Default 1 | 1 | 0 | 1
4 | 12915 | 3273H | 1 | BatSetSOC_H | UInt16 | 0 | % | R/W | Battery Set SOC high |  | Default 80 In grid-connected mode | 80 | 50 | 100
6 | 12916 | 3274H | 1 | BatSetSOC_L | UInt16 | 0 | % | R/W | Battery Set SOC Low |  | Default 40 In grid-connected mode | 40 | 20 | 70
8 | 12917 | 3275H | 1 | CommProtocolType | UInt16 | 0 |  | R/W | Comment Protocol Type |  | 0: Lead-acid battery 1：485 2:DYNESS-can 3：Saj-can 4：pylon-can | 1 | 1 | 3
10 | 12918 | 3276H | 1 | SafetyModeCtrl | UInt16 | 0 |  | R/W | Safety Mode Control |  | Bit 10(DRM Enable bit): 0：OFF 1：ON | 0 | 0 | 4096
12 | 12919 | 3277H | 1 | DRMCertification | UInt16 | 0 | % | R/W | DRM Certification |  | 0:AS4777.2 1:AS4755.3 | 0 | 0 | 1
14 | 12920 | 3278H | 1 | AgingModel | UInt16 | 0 |  | R/W | Aging Model |  | 0:Stand By 1：Charging 2：Discharging | 0 | 0 | 2
16 | 12921 | 3279H | 1 | FeedCtrlPowerLimit | UInt16 | 0 | W | R/W | Feed Control Power Limitation |  | Default 5000W | 5000 | 100 | 6000
| Decimal | Address | SIZE (Word) | Register_Name | Data Type | Rate | Unit | Property | Description about Register | Translate | Note | Defaul ts | Minimum Setting range | Maximum setting range
0 | 13828 | 3604H | 1 | Charge_time_enable_control | Uint16 | 0 |  | R/W | Charge time enable control |  | Each bit is 1 to indicate the number of enabling charging time, the 0th bit is the first one, the 1st bit is the second... | 0 | 0 | 127
2 | 13829 | 3605H | 1 | Discharge_time_enable_control | Uint16 | 0 |  | R/W | Discharge time enable control |  | Each bit is 1 to indicate the number of enabling charging time, the 0th bit. is the first one, the 1st bit is the second… | 0 | 0 | 127
4 | 13830 | 3606H | 1 | First_charge_start_time | HEX | 0 |  | R/W | Battery first charging time (start) |  | High byte is hour, low byte is minute. hh : mm | 0 | 0 | 0x173B(23:59)
6 | 13831 | 3607H | 1 | First_charge_end_time | HEX | 0 |  | R/W | Battery first charging time (end) |  | High byte is hour, low byte is minute. hh : mm | 0 |  | 0x173B(23:59)
8 | 13832 | 3608H | 1 | First_charge_power_time | HEX | 0 |  | R/W | Battery first charging time (power) |  | The high byte indicates the day of the week, and each position is enabled. For example, 0b0100 indicates Wednesday; the low byte indicates power, such as 1 indicates 1% of the standard power of the model
10 | 13833 | 3609H | 1 | Second_charge_start_time | HEX | 0 |  | R/W | Battery second charging time (start) |  | High byte is hour, low byte is minute. hh : mm | 0 | 0 | 0x173B(23:59)
12 | 13834 | 360AH | 1 | Second_charge_end_time | HEX | 0 |  | R/W | Battery second charging time (end) |  | High byte is hour, low byte is minute. hh : mm | 0 |  | 0x173B(23:59)
14 | 13835 | 360BH | 1 | Second_charge_power_time | HEX | 0 |  | R/W | Battery second charging time (power) |  | The high byte indicates the day of the week, and each position is enabled. For example, 0b0100 indicates Wednesday; the low byte indicates power, such as 1 indicates 1% of the standard power of the model
16 | 13836 | 360CH | 1 | Third_charge_start_time | HEX | 0 |  | R/W | Battery third charging time |  | High byte is hour, low byte is minute. is minute. hh : mm | 0 | 0 | 0x173B(23:59)
18 | 13837 | 360DH | 1 | Third_charge_end_time | HEX | 0 |  | R/W | Battery third charging time (end) |  | High byte is hour, low byte is minute. hh : mm | 0 |  | 0x173B(23:59)
20 | 13838 | 360EH | 1 | Third_charge_power_time | HEX | 0 |  | R/W | Battery third charging time (power) |  | The high byte indicates the day of the week, and each position is enabled. For example, 0b0100 indicates Wednesday; the low byte indicates power, such as 1 indicates 1% of the standard power of the model
22 | 13839 | 360FH | 1 | Fourth_charge_start_time | HEX | 0 |  | R/W | Battery fourth charging time (start) |  | High byte is hour, low byte is minute. hh : mm | 0 | 0 | 0x173B(23:59)
24 | 13840 | 3610H | 1 | Fourth_charge_end_time | HEX | 0 |  | R/W | Battery fourth charging time (end) |  | High byte is hour, low byte is minute. hh : mm | 0 |  | 0x173B(23:59)
26 | 13841 | 3611H | 1 | Fourth_charge_power_time | HEX | 0 |  | R/W | Battery fourth charging time (power) |  | The high byte indicates the day of the week, and each position is enabled. For example, 0b0100 indicates Wednesday; the low byte indicates power, such as 1 indicates 1% of the standard power of the model
28 | 13842 | 3612H | 1 | Fifth_charge_start_time | HEX | 0 |  | R/W | Battery fifth charging time (start) |  | High byte is hour, low byte is minute. hh : mm | 0 | 0 | 0x173B(23:59)
30 | 13843 | 3613H | 1 | Fifth_charge_end_time | HEX | 0 |  | R/W | Battery fifth charging time |  | High byte is hour, low byte is minute. hh : mm | 0 |  | 0x173B(23:59)
32 | 13844 | 3614H | 1 | Fifth_charge_power_time | HEX | 0 |  | R/W | Battery fifth charging time (power) |  | The high byte indicates the day of the week, and each position is enabled. For example, 0b0100 indicates Wednesday; the low byte indicates power, such as 1 indicates 1% of the standard power of the model
34 | 13845 | 3615H | 1 | Sixth_charge_start_time | HEX | 0 |  | R/W | Battery sixth charging time (start) |  | High byte is hour, low byte is minute. hh : mm | 0 | 0 | 0x173B(23:59)
36 | 13846 | 3616H | 1 | Sixth_charge_end_time | HEX | 0 |  | R/W | Battery sixth charging time (end) |  | High byte is hour, low byte is minute. hh : mm | 0 |  | 0x173B(23:59)
38 | 13847 | 3617H | 1 | Sixth_charge_power_time | HEX | 0 |  | R/W | Battery sixth charging time (power) |  | The high byte indicates the day of the week, and each position is enabled. For example, 0b0100 indicates Wednesday; the low byte indicates power, such as 1 indicates 1% of the standard power of the model
40 | 13848 | 3618H | 1 | Seventh_charge_start_time | HEX | 0 |  | R/W | Battery seventh charging time (start) |  | High byte is hour, low byte is minute. hh : mm | 0 | 0 | 0x173B(23:59)
42 | 13849 | 3619H | 1 | Seventh_charge_end_time | HEX | 0 |  | R/W | Battery seventh charging time (end) |  | High byte is hour, low byte is minute. hh : mm | 0 |  | 0x173B(23:59)
44 | 13850 | 361AH | 1 | Seventh_charge_power_time | HEX | 0 |  | R/W | Battery seventh charging time (power) |  | The high byte indicates the day of the week, and each position is enabled. For example, 0b0100 indicates Wednesday; the low byte indicates power, such as 1 indicates 1% of the standard power of the model
46 | 13851 | 361BH | 1 | First_discharge_start_time | HEX | 0 |  | R/W | Battery first discharging time (start) |  | High byte is hour, low byte is minute. hh : mm | 0 | 0 | 0x173B(23:59)
48 | 13852 | 361CH | 1 | First_discharge_end_time | HEX | 0 |  | R/W | Battery first discharging time (end) |  | High byte is hour, low byte is minute. hh : mm | 0 |  | 0x173B(23:59)
50 | 13853 | 361DH | 1 | First_discharge_power_time | HEX | 0 |  | R/W | Battery first discharging time (power) |  | The high byte indicates the day of the week, and each position is enabled. For example, 0b0100 indicates Wednesday; the low byte indicates power, such as 1 indicates 1% of the standard power of the model
52 | 13854 | 361EH | 1 | Second_discharge_start_time | HEX | 0 |  | R/W | Battery second discharging time (start) |  | High byte is hour, low byte is minute. hh : mm | 0 | 0 | 0x173B(23:59)
54 | 13855 | 361FH | 1 | Second_discharge_end_time | HEX | 0 |  | R/W | Battery second discharging time (end) |  | High byte is hour, low byte is minute. hh : mm | 0 |  | 0x173B(23:59)
56 | 13856 | 3620H | 1 | Second_discharge_power_time | HEX | 0 |  | R/W | Battery second discharging time (power) |  | The high byte indicates the day of the week, and each position is enabled. For example, 0b0100 indicates Wednesday; the low byte indicates power, such as 1 indicates 1% of the standard power of the model
58 | 13857 | 3621H | 1 | Third_discharge_start_time | HEX | 0 |  | R/W | Battery third discharging time (start) |  | High byte is hour, low byte is minute. hh : mm | 0 | 0 | 0x173B(23:59)
60 | 13858 | 3622H | 1 | Third_discharge_end_time | HEX | 0 |  | R/W | Battery third discharging time (end) |  | High byte is hour, low byte is minute. hh : mm | 0 |  | 0x173B(23:59)
62 | 13859 | 3623H | 1 | Third_discharge_power_time | HEX | 0 |  | R/W | Battery third discharging time (power) |  | The high byte indicates the day of the week, and each position is enabled. For example, 0b0100 indicates Wednesday; the low byte indicates power, such as 1 indicates 1% of the standard power of the model
64 | 13860 | 3624H | 1 | Fourth_discharge_start_time | HEX | 0 |  | R/W | Battery fourth discharging time (start) |  | High byte is hour, low byte is minute. hh : mm | 0 | 0 | 0x173B(23:59)
66 | 13861 | 3625H | 1 | Fourth_discharge_end_time | HEX | 0 |  | R/W | Battery fourth discharging time (end) |  | High byte is hour, low byte is minute. hh : mm | 0 |  | 0x173B(23:59)
68 | 13862 | 3626H | 1 | Fourth_discharge_power_time | HEX | 0 |  | R/W | Battery fourth discharging time (power) |  | The high byte indicates the day of the week, and each position is enabled. For example, 0b0100 indicates Wednesday; the low byte indicates power, such as 1 indicates 1% of the standard power of the model
70 | 13863 | 3627H | 1 | Fifth_discharge_start_time | HEX | 0 |  | R/W | Battery fifth discharging time (start) |  | High byte is hour, low byte is minute. hh : mm | 0 | 0 | 0x173B(23:59)
72 | 13864 | 3628H | 1 | Fifth_discharge_end_time | HEX | 0 |  | R/W | Battery fifth discharging time (end) |  | High byte is hour, low byte is minute. hh : mm | 0 |  | 0x173B(23:59)
74 | 13865 | 3629H | 1 | Fifth_discharge_power_time | HEX | 0 |  | R/W | Battery fifth discharging time (power) |  | The high byte indicates the day of the week, and each position is enabled. For example, 0b0100 indicates Wednesday; the low byte indicates power, such as 1 indicates 1% of the standard power of the model
76 | 13866 | 362AH | 1 | Sixth_discharge_start_time | HEX | 0 |  | R/W | Battery sixth discharging time (start) |  | High byte is hour, low byte is minute. hh : mm | 0 | 0 | 0x173B(23:59)
78 | 13867 | 362BH | 1 | Sixth_discharge_end_time | HEX | 0 |  | R/W | Battery sixth discharging time (end) |  | High byte is hour, low byte is minute. hh : mm | 0 |  | 0x173B(23:59)
80 | 13868 | 362CH | 1 | Sixth_discharge_power_time | HEX | 0 |  | R/W | Battery sixth discharging time (power) |  | The high byte indicates the day of the week, and each position is enabled. For example, 0b0100 indicates Wednesday; the low byte indicates power, such as 1 indicates 1% of the standard power of the model
82 | 13869 | 362DH | 1 | Seventh_discharge_start_time | HEX | 0 |  | R/W | Battery seventh discharging time (start) |  | High byte is hour, low byte is minute. hh : mm | 0 | 0 | 0x173B(23:59)
84 | 13870 | 362EH | 1 | Seventh_discharge_end_time | HEX | 0 |  | R/W | Battery seventh discharging time (end) |  | High byte is hour, low byte is minute. hh : mm | 0 |  | 0x173B(23:59)
86 | 13871 | 362FH | 1 | Seventh_discharge_power_time | HEX | 0 |  | R/W | Battery seventh discharging time (power) |  | The high byte indicates the day of the week, and each position is enabled. For example, 0b0100 indicates Wednesday; the low byte indicates power, such as 1 indicates 1% of the standard power of the model
88 | 13872 | 3630H | 1 | Meter_enable | Uint16 | 0 |  | R/W | Meter enable |  | 0：Off，1：Single meter 2： double meters | 0 | 0 | 2
90 | 13873 | 3631H | 1 | Meter_addr | Uint16 | 0 |  | R/W | Meter address |  | 1 - 255 | 1 | 1 | 255
92 | 13874 | 3632H | 1 | Buzzer_on-off | Uint16 | 0 |  | R/W | Buzzer on-off |  | 0：On，1：Off | 0 | 0 | 1
94 | 13875 | 3633H | 1 | RS485_Addr | Uint16 |  |  | R/W | RS485 Address |  | 1~127 | 1 | 1 | 127
96 | 13876 | 3634H | 1 | RS485_BaudRate | Uint16 |  |  | R/W | RS485 Baud Rate |  | 0:9600,1:4800,2:2400,3:1200 | 0 | 0 | 3
98 | 13877 | 3635H | 1 | PreventReverseFlow enable | Uint16 |  |  | R/W | Prevent Reverse Flow enable |  | 0:Off，1:On
100 | 13878 | 3636H | 1 | Passive_charge_enable | Uint16 |  |  | R/W | Passive charge enable |  | 1：charge；2：discharge
102 | 13879 | 3637H | 1 | Passive_GridChargePower | Uint16 | 0 | w | R/W | The power of grid passive charging
104 | 13880 | 3638H | 1 | Passive_GridDisChargePower | Uint16 | 0 | w | R/W | The power of grid passive discharging
110 | 13883 | 363BH | 1 | Battery_protocol | Uint16 | 0 |  | R/W | Battery protocol |  | 0：pylon RS485-1 1:chint RS485-1 2：Lead acid-0 3:kegon can-3 4:dyness can-2 5：RS485-1 6：pylon can-4 | 0 | 0 | 5